
Headquarters: Acrel Co., Ltd.

Address: 253 Yulv Road , Madong Industrial Park, Jiading, Shanghai

Tel.: 86-21-69158300

Fax: 86-21-69158303

Service hotline: 800-8206632

P.C.: 201801

E-mail: allen@acrel-electric.com
Production base: Jiangsu Acrel Electric Appliances Manufacturing Co., Ltd,

Address: 5 Dongmeng Road , Dongmeng Industrial Park, Nanzha Town, Jiangyin City

Analogue Signal Transducer BM Series

User’s Manual V1.1

Acrel Co., Ltd.

Declaration

The copyright is the property of Acrel. Any information in any paragraph or section cannot be extracted, copied or otherwise reproduced or propagated. Otherwise offenders shall take all consequences.

All rights are reserved.

Acrel reserves the right to modify the product specifications herein without notification. Please consult the local agent about the latest specifications before placing a purchase order.

Contents
1. Overview

1

2. Model and specification

1

3. 2-wire isolator powered by output circuit 

1

4. 1-input/2-output isolator

3

5. 4-wire isolator

4

6. Passive isolator

5

7. 2-wire alternating current isolator powered by output circuit

6

8. 2-wire alternating voltage isolator powered by output circuit

7

9. Smart temperature transducer

8

10. Thermal resistance isolator

9

11. 2-wire resistance isolator powered by output circuit

10

12. 2-wire potentiometer isolator powered by output circuit

11

13. Direct current and voltage alarm with setting point

12

14. Thermal resistance alarm with setting point

13

1. Overview

Analogue signal transducer BM series can measure electrical parameters (e.g. current and voltage) and non-electrical parameters (e.g. temperature and resistance) rapidly and accurately and isolate and convert measured values to standard analogue output signal. It can be not only connected directly with pointer gauges and digital display meters but also integrated with automatic control instruments (e.g. PLC), various A/D converters and computer systems.

2. Model and specification

	Input form
	Input range
	Output range
	Auxiliary supply
	Isolation voltage
	Output settings
	Other features
	Model

	Direct current
	0-1mA

0-20mA

4-20mA

0-5A
	4-20mA
	/
	2kV
	2-wire 8.5-40VDC
	Powered by output circuit
	BM-DI/IS

	Alternating current
	0-1A

0-5A
	4-20mA
	/
	2kV
	2-wire 8.5-40VDC
	Powered by output circuit
	BM-AI/IS

	Direct current
	4-20mA
	4-20mA
	/
	2kV
	Self-powered by input circuit
	
	BM-DIS/I

	
	4-20mA

0-5V
	4-20mA
	24VDC
	2kV
	Independent two circuits
	
	BM-DI/II BM-DV/II BM-DI/IV BM-DV/IV

	
	4-20mA

0-20mA
	4-20mA

0-20mA
	24VDC
	2kV
	4-wire
	
	BM-DI/I

	
	
	
	
	
	
	
	BM-DI/V


	
	
	0-10V;0-5V
	
	
	
	
	

	
	0-20mA
	Two relays controlled by setting point
	110/220V AC, DC
	2kV
	2 NO contact groups
	
	BM-DI/J

	Direct voltage
	0-10V； 0-5V
	4-20mA
	/
	2kV
	2-wire 8.5-40VDC
	Powered by output circuit
	BM-DV/IS

	
	0-10V;0-5V
	4-20mA

0-20mA
	24VDC
	2kV
	4-wire
	
	BM-DV/I

	
	
	
	
	
	
	
	BM-DV/V


	
	
	0-10V;0-5V
	
	
	
	
	

	
	0-10V
	Two relays controlled by setting point
	110/220V AC, DC
	2kV
	2 NO contact groups
	
	BM-DV/J


	Alternating voltage
	0-125V AC

0-250V AC

0-450V AC
	4-20mA
	/
	2kV
	2-wire 8.5-40VDC
	Powered by output circuit
	BM-AV/IS

	Thermocouple

Thermal resistance
	K,J graduation 0-250℃; 0-500℃ 1- 0-1000℃； 0-1200℃
	4-20mA
	24VDC
	2kV
	4-wire
	RS485 communication output
	BM-TC/I BM-TC/V

	Thermal resistance
	Pt100

0-50℃ ;0-100'C 0-150℃; 0-200℃ 0-250℃； 0-300℃
	4-20mA
	/
	2kV
	2-wire 8.5-40VDC
	Powered by output circuit
	BM-TR/IS

	
	
	
	24VDC
	2kV
	4-wire
	
	BM-TR/I

	Resistance
	0-100Ω; 0-lkΩ

0-5kΩ; 0-10kΩ
	4-20mA
	/
	2kV
	2-wire 8.5-40VDC
	Powered by output circuit
	BM-R/IS

	Potentiometer
	0 ~350Ω(~10kΩ)
	4-20mA
	/
	2kV
	2-wire 8.5-40VDC
	Powered by output circuit
	BM-VR/IS


3.  2-wire isolator powered by output circuit 

Application

A 2-wire direct-current isolator powered by output circuit can isolate and convert direct current and voltage signals on site to 4-20mA output signal. The module is equipped with surge protection circuit so that it is suitable under severe conditions.

Specification of product

BM-DI/IS

BM-DV/IS

Overall dimensions

[image: image1.png]



Wiring method

[image: image2.png]56

SF
I

[PLC]

420mA

- |+
8.5~40VDC|





   Output 


   Input 

Technical data

	Technical parameters
	Index

	Input
	Range
	Current: 4-20mA, 0-1mA, 0-20mA

Voltage: 0-1V, 0-5V, 0-10V, 0-75mV, etc

	
	Impedance
	Current: 0(4)-20mA, 100Ω

0-1mA, 1kΩ, voltage≥100Ω

	
	Overload
	Current: 100mA or 1W

Voltage: 50V at 0-10V

	Output
	Range
	DC4~20mA

	
	Load
	<500 Ω

	
	Zero adjustment
	5%

	
	Span adjustment
	5%

	
	Protection
	Short circuit protection

	Power supply
	Range
	Direct voltage: 8.5-40VDC, normally 24VDC/2W

	
	Max. current
	24mA

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature effect
	≤200ppm/℃

	
	Response time
	≤400ms

	
	Isolation voltage
	2kV between input and output

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃

	
	Installation method
	With guide rail TS35


4.  1-input/2-output isolator

Application

The module isolates and converts single-circuit direct current or voltage input signals to mutually-independent two-circuit analogue outputs. It is suitable for the application where a transducer generates one signal circuit to programmer and the other signal circuit to an indicator on site. The module boasts a single input circuit. Therefore, the input voltage drop is almost constant, up to 3.5V and independent from loads. The maximum optocoupler isolation voltage can reach 2kV.

Specification of product

BM-DI/II   BM-DV/II  BM-DI/VI   BM-DV/VI

Overall dimensions

[image: image3.png]76

120

138





Wiring method
[image: image4.png]-1 T+

7

-]+

3
o

1
|





  DC24V or            DC 4-20mA            DC 4-20mA           DC 4-20mA

  AC/DC220V          or DC 0-5V            or DC 0-5V            or DC 0-5V

  Auxiliary supply         Input                 Output 1             Output 2

Technical data

	Technical parameters
	Index

	Input
	Range
	Direct current: 4-20mA, 0-20mA
Direct voltage: DC 0-75mV, 0-5V, 0-10V, 0-300V

	
	Impedance
	Variable, voltage drop up to 3.5V

	
	Overload
	Current: 100mA or 1W

Voltage: 50V at 0-10V

	Output
	Range
	One circuit: DC 4-20mA; the other circuit: DC 4-20mA or DC 0-5V

	
	Load
	Current: ≤500Ω; voltage: ≥1kΩ

	
	Zero adjustment
	15%

	
	Span adjustment
	15%

	Power supply
	Nominal value and range
	DC 24V (alternatively DC 18V-36V)

	Accuracy/linearity
	Max. 0.5% of full span

	Temperature coefficient
	≤200ppm/℃

	Response time
	≤400ms

	Isolation voltage
	2kV between input and each output and between power supply to output

	Surrounding conditions
	Temperature
	Operating temperature: -10 -+55℃; storage temperature: -25 -+70℃

	
	Humidity
	≤95%RH, no condensation, place without corrosive gases

	
	Height above sea level
	≤2000m

	Installation method
	With guide rail TS35


5.  4-wire isolator

Application

A 4-wire isolator provides 2kV 3-port isolation for all direct current and voltage signals and eliminates the earth return. It can be equipped with power supply of various standards.

Features

The size of housing is compact. It can be mounted with guide rail TS35.

Specification of product

BM-DI/I   BM-DI/V    BM-DV/I   DM-DV/V
Overall dimensions

[image: image5.emf]
Wiring method

[image: image6.emf]
Auxiliary supply           Input               Output

Technical data

	Technical parameters
	Index

	Input
	Range
	Current:0-20 mA,4-20 mA,0-1 mA

Voltage:0-5V, 0-10V, 0-300V,0-75mV

	
	Impedance
	Current: 100Ω

Voltage: ≥100Ω

	
	Max. input
	Current: 100mA or 1W

Voltage: 50 VDC

	Output
	Range
	DC4~20mA

	
	Load
	Current: ≤500Ω; voltage: ≥1kΩ

	
	Protection
	Short circuit protection

	
	Zero adjustment (for some modules)
	5%

	
	Span adjustment
	5%

	Power supply
	DC 24V (alternatively DC 18V-36V)

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature coefficient
	≤200ppm/℃

	
	Response time
	≤400ms

	
	Isolation voltage
	2kV between input and output and between input and power supply

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃

	
	Installation method
	With guide rail TS35


6.  Passive isolator

Application

The module converts standard input signals 4-20mA to output signals 4-20mA proportionally via 2kV isolation. It is suitable for applications where it is hard to use the power supply. The input signal powers the module and realizes the coupling via voltage transformer. Therefore, it needs no external power supply.

Specification of product

BM-DIS/I

Overall dimensions

[image: image7.emf]
Wiring method

[image: image8.emf]
   Input                 Output

Technical data

	Technical parameters
	Index

	Input
	Range
	DC4~20mA

	
	Impedance
	Variable; voltage drop: 6V from input load

	
	Max. input
	Current: 30mA

	Output
	Range
	DC4~20mA

	
	Load
	100-400Ω (non-linearity if load is smaller than 100Ω), default: 250Ω

	
	Span adjustment
	Balancing dependent upon output load

	
	Protection
	Short circuit protection

	Power supply
	DC 24V (alternatively DC 18V-36V)

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature coefficient
	≤200ppm/℃

	
	Response time
	≤400ms

	
	Isolation voltage
	2kV between input and output and between input and power supply

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃


7.  2-wire alternating current isolator powered by output circuit

Application

The module can modulate maximum 5A AC or CT current directly and output the isolated 4-20mA signal. The working status and output level of circuit are indicated with LED. The module is equipped with surge protection circuit so that it is suitable under severe conditions.

Specification of product

BM-AI/IS
Overall dimensions

[image: image9.emf]
Wiring method

[image: image10.emf]
   Output            Input

Technical data

	Technical parameters
	Index

	Input
	Range
	AC 0 ~1A or AC 0 ~5A

	
	Impedance
	0.01Ω

	
	Max. input
	1.2 times continuously; 10 times for 1s transiently

	Output
	Range
	DC4-20mA

	
	Load
	≤500Ω

	
	Zero adjustment
	5%

	
	Span adjustment
	5%

	
	Protection
	Short circuit protection

	Power supply
	Range
	8.5-40VDC, normally 24VDC/2W

	
	Max. current
	24mA

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature effect
	≤200ppm/℃

	
	Response time
	≤400ms

	
	Isolation voltage
	2kV between input and output

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃


8.  2-wire alternating voltage isolator powered by output circuit

Application

The module can convert AC voltage (up to 450VAC) to standard isolated output current 4-20mA. It is equipped with surge protection mechanism and suitable for monitoring the startup and stop of motor.

Specification of product

BM-AV/IS
Overall dimensions

[image: image11.emf]
Wiring method

[image: image12.emf]
  Output              Input

Technical data

	Technical parameters
	Index

	Input
	Range
	AC100V, 220V, 380V, 450V

	
	Impedance
	>100kΩ

	
	Max. input
	1.2 times continuously; 10 times for 1s transiently

	Output
	Range
	DC4-20mA

	
	Load
	≤500Ω

	
	Zero adjustment
	5%

	
	Span adjustment
	5%

	
	Protection
	Short circuit protection

	Power supply
	Range
	8.5-40VDC, normally 24VDC/2W

	
	Max. current
	24mA

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature effect
	≤200ppm/℃

	
	Response time
	≤400ms

	
	Isolation voltage
	2kV between input and output

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃


9.  Smart temperature transducer

Application

The module receives inputs from thermocouple and thermal resistance and outputs signals DC0-20mA, 4-20mA, 0-5V or 0-10V linearly and proportionally. It boasts the automatic cold junction compensation (CJC), a surge protection circuit and RS485 communication ports. It can be connected with an external programmer to set parameters and indicate temperature. 

Specification of product

BM-TC/I  BM-TC/V
Overall dimensions

[image: image13.emf]
Wiring method

[image: image14.emf]
Auxiliary supply       Input            Output      Communication

Technical data

	Technical parameters
	Index

	Input
	Type
	Thermocouple (J, K, B, R, S, T, E, N), thermal resistance (PT100, Cu50)

	
	Range
	-200℃~1300℃

	Output
	Range
	DC4~20mA、 0~20mA、 0~5V、 0~10V

	
	Load
	Current: ≤500Ωor voltage: ≥1kΩ

	
	Protection
	Short circuit protection

	Power supply
	Range
	24DC（alternatively 18-36V）

	
	Max. current
	0.5% of full span

	Other
	Accuracy/linearity
	±0.3℃

	
	Temperature effect
	≤200ppm/℃

	
	Response time
	≤400ms

	
	Isolation voltage
	2kV between input and output

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃


10.  Thermal resistance isolator

Application

The module receives inputs from RTD and outputs 2kV-isolated signals 4-20mA proportionally. It is equipped with surge protection circuit so that it is suitable under severe conditions.

Specification of product

BM-TR/IS   BM-TR/I   BM-TR/V
Overall dimensions

[image: image15.emf]
Wiring method

BM-TR/I   BM-TR/V
[image: image16.png][s]a]3]

[s]a]3

1

o

4-20mA




Auxiliary supply  3-wire RTD input   2-wire RTD input        Output

BM-TR/IS
[image: image17.emf]
3-wire RTD input   2-wire RTD input   Output
Technical data

	Technical parameters
	Index

	Input
	Range
	2-wire or 3-wire RTD Pt100 (α=0.00385), -100℃-300℃

	
	Other features
	Linearly dependent upon temperature

	Output
	Range
	DC 4~20mA、 0~5V、 0~10V

	
	Load
	Current: ≤500Ω or voltage: ≥1kΩ

	
	Zero adjustment
	5%

	
	Span adjustment
	5%

	
	Protection
	Short circuit protection

	Power supply
	Range
	8.5-40VDC, normally 24VDC/2W

	
	Max. current
	24mA

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature effect
	≤200ppm/℃

	
	Response time
	≤400ms

	
	Isolation voltage
	2kV between input and output

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃


11.  2-wire resistance isolator powered by output circuit

Application

It can provide the output 4-20mA and 2000V isolation for standard 2-wire resistance signal. Its accuracy is higher than 0.5%.

Specification of product

BM-R/IS
Overall dimensions

[image: image18.emf]
Wiring method

[image: image19.emf]
  Output                             Input

Technical data

	Technical parameters
	Index

	Input
	Range
	0-100Ω, 0-lkΩ, 0-5 kΩ, 0-10 kΩ

	
	Protection type
	Zener diode

	Output
	Range
	4-20mA

	
	Load
	0-775 Q, Rmax=(Vs-8. 5/0. 02) Q

	
	Load influence
	<0.1%

	
	Protection
	Short circuit protection

	
	Zero adjustment
	Min. 5%

	
	Span adjustment
	Min. 5%

	Power supply
	Range
	8.5-40VDC, normally 24VDC/2W

	
	Max. current
	24mA

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃


12.  2-wire potentiometer isolator powered by output circuit

Application

A potentiometer isolator can provide the output 4-20mA and 2kV isolation for potentiometers ranging from 350Ω to 10kΩ. It accuracy reaches the class 0.5.

Specification of product

BM-VR/IS
Overall dimensions

[image: image20.emf]
Wiring method

[image: image21.emf]
   Output                           Input

Technical data

	Technical parameters
	Index

	Input
	Range
	0 ~350Ω (~10kΩ)

	
	Default setting
	0 ~1kΩ

	
	Protection type
	Zener diode

	Output
	Range
	DC4-20mA

	
	Load
	≤500Ω

	
	Load influence
	<0.1%

	
	Protection
	Short circuit protection

	
	Zero adjustment
	5%

	
	Span adjustment
	5%

	Power supply
	Range
	8.5-40VDC, normally 24VDC/2W

	
	Max. current
	24mA

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃

	
	Temperature drift
	≤200ppm/℃

	
	Isolation
	2kV between input and output


13.  Direct current and voltage alarm with setting point

Application

It receives the direct current or voltage input and provides a dual-channel alarm output. It sends an alarm if a current or voltage signal exceeds its limit. Set an alarm point between 0% and 100% of input. The alarm point has a hysteresis error of 1% to eliminate the influence of relay contact chatter. The LED in the front can indicate the status of relay. The module can work as auxiliary supply DC24V (Imax =50mA) on site.

Specification of product

BM-DI/J   BM-DV/J
Overall dimensions

[image: image22.emf]
Wiring method

[image: image23.png]omomoe

ALL



  
Auxiliary supply         Input        DC24V output       Relay output


Technical data

	Technical parameters
	Index

	Input
	Range
	0~20mA / 0~10VDC

	
	Impedance
	50Ω/1MΩ

	
	Max. input/ protection type
	100mA or 1W/Zener diode 50VDC

	
	Field excitation
	Max. 24VDC, 25mA

	Output
	Output range
	Two independent relays, with high/ low jumper setting

	
	Contact load
	10A 250VAC/30VDC (resistive load)

	
	Adjustment of setting point
	0-100% of input span

	
	Alarm function
	High (forward)/ low (reserve) alarm

	
	Protection
	Additional protection is required if relay contacts are used to connect or disconnect inductive loads.

	
	Dead zone
	Hysteresis error: 1% of full span

	Power supply
	Range
	AC85 ~265V or DC100V ~350V

	
	Power consumption
	< 20mA AC (2VA)

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature effect
	< 0. 02% /℃

	
	Response time
	(90% of span) <100ms

	
	Status of LED
	A red LED is equipped with each relay. (The LED turns on if its corresponding relay is activated.)

	
	Isolation
	2kV

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃


14.  Thermal resistance alarm with setting point

Application

It receives inputs from thermal resistance PT100 and provides a dual-channel alarm output. Set an alarm point between 0% and 100% of input. The alarm point has a hysteresis error of 1% to eliminate the influence of relay contact chatter. The LED in the front can indicate the status of relay. The module can work as auxiliary supply DC24V (Imax =50mA) on site. Set an (forward) or low (reverse) alarm with the jumper on the top.

Specification of product

BM-TR/J
Overall dimensions

[image: image24.emf]
Wiring method

[image: image25.png]]

™
AL1

"

I?WI [8][o]0l[L1]




Auxiliary supply  3-wire RTD input  2-wire RTD input   DC24V output      Relay output

Technical data

	Technical parameters
	Index

	Input
	Input type
	Thermal resistance PT100

	
	Input range
	0~300℃

	
	Impedance
	10MΩ

	
	Max. input/ protection type
	100mA or 1W/Zener diode 50VDC

	
	Field excitation
	Max. 24VDC, 25mA

	Output
	Output range
	Two independent relays (NO contact)

	
	Contact load
	10A 250VAC/30VDC (resistive load)

	
	Adjustment of setting point
	0-100% of input span

	
	Alarm function
	High (forward)/ low (reserve) alarm

	
	Protection
	Additional protection is required if relay contacts are used to connect or disconnect inductive loads.

	
	Dead zone
	Hysteresis error: 1% of full span

	Power supply
	Range
	AC85 ~265V or DC100V ~350V

	
	Power consumption
	< 20mA AC (2VA)

	Other
	Accuracy/linearity
	Max. 0.5% of full span

	
	Temperature effect
	≤200ppm/℃

	
	Response time
	(90% of span) <100ms

	
	Status of LED
	A red LED is equipped with each relay. (The LED turns on if its corresponding relay is activated.)

	
	Isolation
	Input/ output/ power supply 2kV

	
	Operating/storage temperature
	-10℃ ~+55℃/-25 ~+70℃



